## Arc-Flash Review
ServiceCycle - Arc-Flash Data Model: PE Review
ServiceCycle is becoming the place a facility STORES, TRACKS, and MANAGES every data point from their arc-flash studies over time. We drafted the data set below from NFPA 70E-2024 and IEEE 1584-2018. You are the accuracy check - confirm our terms, values, units, and rules match how studies are actually run. You are NOT deciding what a customer keeps (they decide that); just whether the standards-based pieces are right.
HOW TO USE: In each row put Y or N in the 'OK?' column (it's a dropdown). If N, type the fix in 'Your notes'. Grey rows are open - add anything we are missing. Class key: REQ = needed to run the calc, TYP = can default by equipment type, OUT = a result/label value, MIT = mitigation/context.
1. Equipment classes + their typical defaults (we pre-fill these IEEE 1584-2018 typicals; a PE can override)
Item | Typical electrode / gap (mm) / working distance (in) | OK? (Y/N) | Your notes / fixes / additions
LV panelboard (<=600 V) | VCB / 25 / 18
LV MCC | VCB (HCB if horizontal bus) / 25 / 18
LV switchgear (600 V) | VCB / 32 / 24
Cable / cable junction | VCB / 13 / 18
5 kV switchgear | VCB / 104 / 36
15 kV switchgear | VCB / 152 / 36
Open-air bus | VOA or HOA / gap by voltage / task-specific
MISSING - equipment classes we don't list:
2. Electrode configurations (we store these 5 as a fixed list)
Item | Meaning | OK? (Y/N) | Your notes / fixes / additions
VCB | Vertical conductors in a box
VCBB | Vertical conductors ending at an insulating barrier, in a box
HCB | Horizontal conductors in a box
VOA | Vertical conductors in open air
HOA | Horizontal conductors in open air
Some sources write 'VCCB' for VCBB - we standardized on VCBB. Correct? | (Y/N, note any preference)
3. Protective devices - what a tech records, and WHEN settings are required *** most important section ***
Item | Fields we'd record ¦ Settings required? | OK? (Y/N) | Your notes / fixes / additions
Fuse (any class) | class, amp rating, voltage, mfr, model ¦ NO (clearing from class+rating via TCC)
MCCB - thermal-magnetic | frame A, trip rating A, mfr, model, (adj. instantaneous if present) ¦ NO (fixed; TCC from rating)
MCCB - electronic trip (LSI/LSIG) | frame A, sensor/plug A, mfr, model, LSIG settings ¦ YES
Insulated-case breaker (ICCB) | frame A, sensor A, mfr, model, LSIG settings, ERMS? ¦ YES
LV power breaker (LVPCB / air-frame) | frame A, sensor A, mfr, model, LSIG settings, ERMS? ¦ YES
Relay + breaker (MV, or relayed LV) | ANSI device #s, CT ratio, relay settings, breaker mfr/model ¦ YES
CONFIRM THE RULE: Settings are required ONLY for adjustable devices (electronic LSI/LSIG + relays). Fuses, thermal-mag breakers, and switches have NO settings - type + rating is the complete record, clearing time comes off the published TCC. | (Y/N - if wrong or has exceptions, explain in notes)
MISSING - device families or fields you always record:
4. Fuse classes
Item | Current-limiting? | OK? (Y/N) | Your notes / fixes / additions
Class L | Yes
Class RK1 | Yes
Class RK5 | Yes
Class J | Yes
Class T | Yes
Class CC | Yes
Class G | Yes
Class CF | Yes
Class H | No
Class K | Yes
MISSING - fuse classes we don't list:
5. Relay functions (ANSI device numbers) a tech can record
Item | Settings we capture | OK? (Y/N) | Your notes / fixes / additions
50 Instantaneous overcurrent | pickup
51 Time overcurrent | pickup, time dial, curve type
50G / 50N Inst. ground/neutral | pickup
51G / 51N Time ground/neutral | pickup, time dial, curve
87 Differential | zone, slope, pickup
50AF / fast-bus Arc-flash relay | light setpoint, current supervision, trip time
MISSING - relay functions you set in the field:
6. Mitigation we capture (changes the result / drives a 2nd label state)
Item | What we capture | OK? (Y/N) | Your notes / fixes / additions
ERMS / maintenance mode | present?, reduced instantaneous pickup, reduced energy (cal/cm2)
Zone-selective interlocking (ZSI) | enabled?
Differential relaying (87) | present?, zone
Arc-resistant switchgear | rated?, standard, doors-open vs doors-closed
NEC 240.87 (trip setting >= 1200 A) | which method + its setting
MISSING - mitigation types:
7. Units + sane ranges (so we can catch fat-finger entries)
Item | Unit we store ¦ Proposed normal range | OK? (Y/N) | Your notes / fixes / additions
Nominal voltage | V ¦ 120 to 38,000
Bolted fault current | kA ¦ 0.5 to 106
Arcing current | kA ¦ 0.2 to 100
Conductor gap | mm ¦ 6 to 254
Working distance | in ¦ 12 to 48
Clearing time | ms ¦ 8 to 2,000
Incident energy | cal/cm2 ¦ 0.1 to 200
Arc-flash boundary | in ¦ 1 to 600
Required arc rating (ATPV/EBT) | cal/cm2 ¦ 4 to 100
Enclosure height / width / depth | mm ¦ 100 to 1,500
Shock: limited / restricted approach | in ¦ 0 to 120
Any value stored in the wrong unit, or a range that's off:
8. Required vs typical vs outcome (did we classify each correctly?)
Item | Our classification (REQ / TYP / OUT) | OK? (Y/N) | Your notes / fixes / additions
Nominal voltage | REQ
Bolted fault current (or feeder cable to compute it) | REQ
Upstream device + (settings only if adjustable) | REQ
Electrode config | TYP - default by class
Conductor gap | TYP
Working distance | TYP
Enclosure type + dimensions | TYP (REQ for the size correction)
Utility max + min fault + X/R | REQ (system)
Transformer kVA / %Z / connection | REQ (system)
Incident energy, AF boundary, PPE, arc rating | OUT
Anything classified wrong:
9. Source / system inputs (feed the fault-current calc)
Item | Fields we capture | OK? (Y/N) | Your notes / fixes / additions
Utility / service | available fault MAX, MIN, and X/R
Transformer | kVA, primary V, secondary V, %Z, X/R, connection
Motors | total HP + count (no 50 HP exemption in 2018)
Generators | kVA, V, subtransient reactance
Cable / feeder | length, size, material (Cu/Al), # per phase, conduit type
MISSING - source data:
10. Results, label, and DANGER/WARNING - confirm
Item | What we do | OK? (Y/N) | Your notes / fixes / additions
We capture BOTH PPE approaches (incident-energy method AND the PPE-category table method) and store which one a label uses. | (Y/N)
Label fields (NFPA 70E 130.5(H)) we store: nominal voltage, arc-flash boundary, incident energy + working distance OR arc rating OR PPE category, study date, shock boundaries, equipment ID. | (note anything missing)
We flag DANGER when incident energy > 40 cal/cm2 OR voltage > 600 V, else WARNING. | (Y/N - correct threshold?)
11. Bottom line
Item |  | OK? (Y/N) | Your notes / fixes / additions
Are we capturing the right overall set of data for a real study? | Yes / Mostly / No (use the dropdown)
The single most important thing we're missing:
Anything that would make this genuinely useful to you and other engineers (contractor or in-house), at any experience level: